{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Data list","MOV template"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Data list","index":0,"n_rows":30,"n_cols":18,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
["Item","Tag Number\n(from instrument list)","Service\n(from instrument list)","Valve Type\n(from P&ID)","PID\n(from instrument list)","line no.\n(from instrument list)","Fluid\n(by process department)","Line Size (inches)","Pipe Class","ANSI Class\n(from PMS, min=300#)","Pipe Schedule\n(from PMS)","Flange Face & Finish\n(from PMS)","Line Insulation\n(from PMS)","Body Material\n(from PMS)","Leakage / Shot Off Class\n( P&ID)","Construction\n(from spec)","Bolts & Nuts\n( Spec)","Power Supply\n( Sped & Electrical Department)"]
[1,"1255-MOV-0001","Sweet Gas From 1255-D-102 To UNIT 104","Butterfly","1255-45-0104","26\"-G.1255.10022-F23S-N","Hydrocarbon Gas",26,"F23S","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","VI (TSO)","Lug Connection","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[2,"1255-MOV-0002","1255-X-101 To 1255-E-102","Butterfly","1255-45-0108","18\"-SL.1255.12104-B12-H","Low Pressure Steam",18,"B12","300#","S-20","RF (125-250 AARH)","Hot Insulation","A 351 CF8","VI (TSO)","Lug Connection","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[3,"1255-MOV-0003","1255-P-104 A/B To 1255-D-105","Ball (Trunnion Mounted)","1255-45-0108","3\"-CL.1255.12104-D01-P","LP Steam Condensate",3,"D01","300#","STD","RF (125-250 AARH)","Personel Protection","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[4,"1255-MOV-0004","1255-P-102 A/B Disch.To 1255-D-104","Ball (Trunnion Mounted)","1255-45-0109","2\"-AM.1255.10110-B03S-N","Amine",2,"B03S","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[5,"1255-MOV-0005","1255-P-101 A/BTo 1255-C-101","Ball (Trunnion Mounted)","1255-45-0110","10\"-AM.1255.10031-F03N-N","Amine",10,"F03N","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[6,"1255-MOV-0006","1255-P-101A/B To 1255-C-103","Ball (Trunnion Mounted)","1255-45-0110","2\"-AM.1255.10059-F03N-N","Amine",2,"F03N","300#","S-80","RF (125-250 AARH)","None","A 182 F304","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[7,"1255-MOV-0007","1255-P-101A/B To 1255-T-101","Ball (Trunnion Mounted)","1255-45-0110","3\"-AM.1255.10112-F03N-N","Amine",3,"F03N","300#","STD","RF (125-250 AARH)","None","A 351 CF8","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[8,"1255-MOV-0008","Filtration PackageBypass","Ball (Trunnion Mounted)","1255-45-0111A","3\"-AM.1255.10135-B03N-N","Amine",3,"B03N","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[9,"1255-MOV-0009","1255-P-101 A/BTo 1255-D-103","Ball (Trunnion Mounted)","1255-45-0105","6\"-AM.1255.10033-F03N-N","Amine",6,"F03N","300#","STD","RF (125-250 AARH)","None","A 351 CF8","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[10,"1255-MOV-0010","1255-D-101 To 103-D-101","Ball (Trunnion Mounted)","1255-45-0101","2\"-L.1255.10016-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[11,"1255-MOV-0011","1255-F-101","Ball (Trunnion Mounted)","1255-45-0102","2\"-L.1255.10004-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","Hot Insulation","A 350 LF2","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[12,"1255-MOV-0012","1255-F-101","Ball (Trunnion Mounted)","1255-45-0102","2\"-L.1255.10005-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[13,"1255-MOV-0013","1255-C-101To 1255-D-103","Ball (Trunnion Mounted)","1255-45-0103","10\"-AM.1255.10002-F48-N","Amine",10,"F48","300#","S-20","RF (125-250 AARH)","None","A216 WCC","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[14,"1255-MOV-0014","1255-C-101 To 1255-D-103","Ball (Trunnion Mounted)","1255-45-0103","2\"-AM.1255.10098-F48-N","Amine",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[15,"1255-MOV-0015","1255-D-102 To 1255-D-103","Ball (Trunnion Mounted)","1255-45-0104","3\"-AM.1255.10006-F48-N","Amine",3,"F48","300#","STD","RF (125-250 AARH)","None","A216 WCC","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[16,"1255-MOV-0016","1255-E-101 A/B/CTo 1255-C-102","Ball (Trunnion Mounted)","1255-45-0107","12\"-AM.1255.10012-B48-H","Amine",12,"B48","600#","S-20","RF (125-250 AARH)","Hot Insulation","A216 WCC","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[17,"1255-MOV-0017","1255-E-103To 1255-T-101","Ball (Trunnion Mounted)","1255-45-0106","14\"-AM.1255.10014-B03N-N","Amine",14,"B03N","300#","S-20","RF (125-250 AARH)","None","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[18,"1255-MOV-0018","1255-P-104BDischarge","Ball (Trunnion Mounted)","1255-45-0108","4\"-CL.1255.12103-D01-P","LP Steam Condensate",4,"D01","300#","STD","RF (125-250 AARH)","Personel Protection","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[19,"1255-MOV-0019","1255-P-102 A/B To 1255-C-102","Ball (Trunnion Mounted)","1255-45-0109","3\"-AM.1255.10023-B03S-N","Amine",3,"B03S","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[20,"1255-MOV-0020","Sweet Gas From 1255-D-102 To UNIT 104","Butterfly","1255-45-0104","20\"-G.1255.10018-F23S-N","Hydrocarbon Gas",20,"F23S","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","VI (TSO)","Lug Connection","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[21,"1255-MOV-0021","1255-C-103To Steam Boilers","Ball (Trunnion Mounted)","1255-45-0105","3\"-G.1255.10011-B03S-H","Hydrocarbon Gas",3,"B03S","300#","STD","RF (125-250 AARH)","Hot Insulation","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[22,"1255-MOV-0022","1255-C-103To FS22","Ball (Trunnion Mounted)","1255-45-0105","3\"-G.1255.10013-B03S-S","Hydrocarbon Gas",3,"B03S","300#","STD","RF (125-250 AARH)","Steam Tracing","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[23,"1255-MOV-0023","Fuel GasTo Flash Gas ","Ball (Trunnion Mounted)","1255-45-0105","2\"-FG.1255.12202-D01-N","Fuel Gas",2,"D01","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[24,"1255-MOV-0024","NitrogenTo 1255-C-102 outlet","Ball (Trunnion Mounted)","1255-45-0107","4\"-N.1255.12402-B01-N","Nitrogen",4,"B01","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[25,"1255-MOV-0025","1255-D-104 outletTo FS22","Ball (Trunnion Mounted)","1255-45-0109","10\"-GA.1255.10006-B03S-S","Acid Gas (H2S+CO2)",10,"B03S","300#","S-20","RF (125-250 AARH)","Steam Tracing","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[26,"1255-MOV-0026","Acid Gas from 1255-D-104To Sulfur Recovery  U108","Ball (Trunnion Mounted)","1255-45-0109","14\"-GA.1255.10003-B03S-H","Acid Gas (H2S+CO2)",14,"B03S","300#","S-20","RF (125-250 AARH)","Hot Insulation","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[27,"1255-MOV-0027","1255-C-101To 1255-D-102","Butterfly","1255-45-0104","24\"-G.1255.10019-F23S-H","Hydrocarbon Gas",24,"F23S","300#","S-20","RF (125-250 AARH)","Hot Insulation","A 351 CF8","VI (TSO)","Lug Connection","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]
[28,"1255-MOV-0028","1255-E-103 ByPass","Ball (Trunnion Mounted)","1255-45-0106","14\"-AM.1255.10054-B03N-N","Amine",14,"B03N","300#","S-20","RF (125-250 AARH)","None","ASTM A 216WCB","VI (TSO)","Reduced, Split Body","ASTM A193 B7M / A194 Gr. 2HM","AC 400V, 3Ph., 50Hz"]
[29,"1255-MOV-0029","CCTo 1255-X-101 ","Ball (Trunnion Mounted)","1255-45-0108","2\"-CC-101-12101-D01-N","Cold Steam Condensate",2,"D01","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","VI (TSO)","Reduced, Split Body","ASTM A193 B7 / A194 Gr. 2H","AC 400V, 3Ph., 50Hz"]

{"sheet":"MOV template","index":1,"n_rows":74,"n_cols":35,"rows_kept":74,"cut":false,"hidden":false,"merged":[[47,0,66,2],[34,3,34,14],[35,3,35,14],[36,3,36,14],[37,3,37,14],[38,6,38,14],[39,6,39,14],[40,6,40,14],[41,6,41,14],[42,6,42,14],[38,3,46,5],[10,15,10,29],[11,15,11,29],[12,15,12,29],[13,15,13,29],[14,15,14,29],[15,15,15,29],[16,15,16,29],[17,15,17,29],[18,15,18,29],[19,15,19,29],[20,15,20,29],[21,15,21,29],[22,15,22,29],[23,15,23,29],[24,15,24,29],[25,15,25,29],[26,15,26,29],[27,15,27,29],[28,15,28,29],[29,15,29,29],[30,15,30,29],[31,15,31,29],[62,15,62,29],[63,15,63,29],[64,15,64,29],[65,15,65,29],[66,15,66,29],[62,3,62,14],[63,3,63,14],[64,3,64,14],[65,3,65,14],[66,3,66,14],[57,15,57,29],[58,15,58,29],[59,15,59,29],[60,15,60,29],[61,15,61,29],[57,3,57,14],[58,3,58,14],[59,3,59,14],[60,3,60,14],[61,3,61,14],[52,15,52,29],[53,15,53,29],[54,15,54,29],[55,15,55,29],[56,15,56,29],[52,3,52,14],[53,3,53,14],[54,3,54,14],[55,3,55,14],[56,3,56,14],[47,15,47,29],[48,15,48,29],[49,15,49,29],[50,15,50,29],[51,15,51,29],[47,3,47,14],[48,3,48,14],[49,3,49,14],[50,3,50,14],[51,3,51,14],[42,15,42,29],[43,15,43,29],[44,15,44,29],[45,15,45,29],[46,15,46,29],[43,6,43,14],[44,6,44,14],[45,6,45,14],[46,6,46,14],[30,0,46,2],[19,0,29,2],[10,3,10,14],[13,3,13,14],[14,3,14,14],[9,46,9,55],[0,0,8,6],[0,7,4,22],[5,7,6,9],[5,10,6,22],[7,7,8,10],[7,11,8,22],[9,0,9,29],[16,3,16,14],[17,3,17,14],[18,3,18,14],[19,3,19,14],[21,3,21,14],[22,3,22,14],[23,3,23,14],[24,3,24,14],[33,15,33,29],[34,15,34,29],[35,15,35,29],[36,15,36,29],[37,15,37,29],[38,15,38,29],[39,15,39,29],[40,15,40,29],[41,15,41,29],[25,3,25,14],[26,3,26,14],[27,3,27,14],[28,3,28,14],[68,2,68,28],[11,3,11,14],[12,3,12,14],[32,15,32,29],[29,3,29,14],[30,3,30,14],[31,3,31,14],[32,3,32,14],[33,3,33,14],[10,0,18,2],[15,3,15,14],[20,3,20,14],[7,24,8,25],[0,23,6,29],[69,2,69,28],[70,2,70,28],[71,2,71,28],[72,2,72,28],[73,2,73,28],[7,26,8,27],[7,28,8,29],[7,23,8,23]]}
["Client Logo",null,null,null,null,null,null,"Project Title",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Consultant Logo"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,"Doc Title :"]
[]
[null,null,null,null,null,null,null,"Doc. Number : ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Rev.:",0,null,"Page no.: "]
[]
["Motor Operated Valve Datasheet"]
["GENERAL",null,null," 1. Tag No."]
[null,null,null," 2. P & ID No.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"                                                                                                                                                                                                                                                 "]
[null,null,null," 3. Service "]
[null,null,null," 4. Line No. "]
[null,null,null," 5. Pipe Class / Pipe Schedule / Line Insulation"]
[null,null,null," 6. Type of Valve"]
[null,null,null," 7. Fail Action",null,null,null,null,null,null,null,null,null,null,null,"Last Position"]
[]
[]
["PROCESS\nDATA",null,null," 8. Fluid  L ; Liquid, G ; Gas, V ; Vapor,S ; Steam"]
[null,null,null," 9. Flow Rate  : Kg/h"]
[null,null,null,"10. Pressure   Design / Operating       (bar g)"]
[null,null,null,"11. Max. Pressure Drop                      (bar)"]
[null,null,null,"12. Temperature  Design / Operating   (℃)"]
[null,null,null,"13. Density  (Kg/㎥)  /  Mol. Wg't"]
[null,null,null,"14. Operating Viscosity                        (cp)"]
[null,null,null,"15. Up / Downstream Press. ",null,null,null,null,null,null,"Valve to Open"]
[null,null,null,"16.Max. Difference     (bar)",null,null,null,null,null,null,"Valve to Close"]
[null,null,null,"17. Stroking time from 'FO' to 'FC'"]
[]
["VALVE",null,null,"18. Construction"]
[null,null,null,"17. Body Size (inch) / Bore Size (inch) "]
[null,null,null,"20. End Conn. & Rating "]
[null,null,null,"21. Required Tightness"]
[null,null,null,"22. Seat Type",null,null,null,null,null,null,null,null,null,null,null,"Renewable"]
[null,null,null,"23. Bonnet Type",null,null,null,null,null,null,null,null,null,null,null,"Bolted"]
[null,null,null,"24. Trim Form",null,null,null,null,null,null,null,null,null,null,null,"On-Off"]
[null,null,null,"25. Bi-Directional",null,null,null,null,null,null,null,null,null,null,null,"Yes"]
[null,null,null,"26. Material",null,null,"- Body / Bonnet & Cover"]
[null,null,null,null,null,null,"- Ball /Disc /Plug",null,null,null,null,null,null,null,null,"316SS (VTC)"]
[null,null,null,null,null,null,"- Stem",null,null,null,null,null,null,null,null,"316SS (VTC)"]
[null,null,null,null,null,null,"- Seat / Seat Insert",null,null,null,null,null,null,null,null,"316SS (VTC)"]
[null,null,null,null,null,null,"- Static & Dynamic Seal",null,null,null,null,null,null,null,null,"VTA"]
[null,null,null,null,null,null,"- Fire-Safe back-up Seals / Gaskets",null,null,null,null,null,null,null,null,"Graphite / Graphite "]
[null,null,null,null,null,null,"- Seat Spring",null,null,null,null,null,null,null,null,"316SS (VTC)"]
[null,null,null,null,null,null,"- Bearings",null,null,null,null,null,null,null,null,"316SS (VTC)"]
[null,null,null,null,null,null,"- Bolt / Nuts"]
["MOTOR\nACTUATOR",null,null,"27. Type",null,null,null,null,null,null,null,null,null,null,null,"INTEGRAL"]
[null,null,null,"28. Power Supply"]
[null,null,null,"29. Insulation",null,null,null,null,null,null,null,null,null,null,null,"CLASS  F"]
[null,null,null,"30. Enclosure",null,null,null,null,null,null,null,null,null,null,null,"EExd IIB T3  & IP65"]
[null,null,null,"31. Rated Horse Power",null,null,null,null,null,null,null,null,null,null,null,"VTA"]
[null,null,null,"32. Rated Speed",null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,null,null,"33. Full Load Current",null,null,null,null,null,null,null,null,null,null,null,"VTA"]
[null,null,null,"34. Cable Entry No. & Size",null,null,null,null,null,null,null,null,null,null,null,"2×M25 ISO, 1×M20 ISO w/ plug "]
[null,null,null,"35. Thermostat",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"36. Torque Switch / Limit Switch (ON/OFF)",null,null,null,null,null,null,null,null,null,null,null,"YES / YES "]
[null,null,null,"37. Position Indicator",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"38. Phase Discriminator",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"39. Monitor Relay",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"40. Reversing Contact Starter",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"41. Selector Switch       (LOCAL / REMOTE)",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"42. Push-button            (OPEN / STOP / CLOSE)",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"43. Handwheel",null,null,null,null,null,null,null,null,null,null,null,"YES"]
[null,null,null,"44. Space Heater",null,null,null,null,null,null,null,null,null,null,null,"Provided with internal electrical component"]
[null,null,null,"45. Valve Mfr. & Model No."]
[null,null,null,"46. Actuator Mfr. & Model No."]
[]
[null,"1."," VTA: Vendor To Advise   VTC: Vendor To Confirm  N/A: Not Applicable"]
[null,"2."]
[null,"3."]
[null,"4."]
[null,"5."]
[null,"6."]