{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Data list","OnOff template"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Data list","index":0,"n_rows":30,"n_cols":21,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
["Item","Tag Number\n(from instrument list)","Service\n(from instrument list)","Valve Type\n(from P&ID)","PID\n(from instrument list)","line no.\n(from instrument list)","Fluid\n(by process department)","Line Size (inches)","Pipe Class","ANSI Class\n(from PMS, min=300#)","Pipe Schedule\n(from PMS)","Flange Face & Finish\n(from PMS)","Line Insulation\n(from PMS)","Body Material\n(from PMS)"," Valve  Action\n(from instrument list / P&ID)","Leakage / Shot Off Class\n( P&ID)","Trim Type\n(from spec)","Handwheel \n( P&ID)","Switch Tag nO.\n( P&ID)","Solenoid Tag no.\n( P&ID)","Air Accumulation Tank\n(from spec)"]
[1,"1255-SDV-0036","Sweet Gas From 1255-D-102 To UNIT 104","Butterfly","1255-45-0104","26\"-G.1255.10022-F23S-N","Hydrocarbon Gas",26,"F23S","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","FC (Fail Close)","V","Reduced Bore","No","1255-SZSO/C-0036","1255-SDX-0036","No"]
[2,"1255-SDV-0071","1255-X-101 To 1255-E-102","Butterfly","1255-45-0108","18\"-SL.1255.12104-B12-H","Low Pressure Steam",18,"B12","300#","S-20","RF (125-250 AARH)","Hot Insulation","A 351 CF8","FC (Fail Close)","V","Reduced Bore","Yes","1255-SZSO/C-0071","1255-SDX-0071","No"]
[3,"1255-SDV-0077","1255-P-104 A/B To 1255-D-105","Ball","1255-45-0108","3\"-CL.1255.12104-D01-P","LP Steam Condensate",3,"D01","300#","STD","RF (125-250 AARH)","Personel Protection","ASTM A 216WCB","FO (Fail Open)","V","Reduced Bore","No","1255-SZSO/C-0077","1255-SDX-0077","No"]
[4,"1255-SDV-0083","1255-P-102 A/B Disch.To 1255-D-104","Ball","1255-45-0109","2\"-AM.1255.10110-B03S-N","Amine",2,"B03S","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","FO (Fail Open)","V","Reduced Bore","No","1255-SZSO/C-0083","1255-SDX-0083","No"]
[5,"1255-SDV-0086","1255-P-101 A/BTo 1255-C-101","Ball","1255-45-0110","10\"-AM.1255.10031-F03N-N","Amine",10,"F03N","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","FC (Fail Close)","V","Reduced Bore","No","1255-SZSO/C-0086","1255-SDX-0086","No"]
[6,"1255-SDV-0088","1255-P-101A/B To 1255-C-103","Ball","1255-45-0110","2\"-AM.1255.10059-F03N-N","Amine",2,"F03N","300#","S-80","RF (125-250 AARH)","None","A 182 F304","FC (Fail Close)","V","Reduced Bore","No","1255-SZSO/C-0088","1255-SDX-0088","No"]
[7,"1255-SDV-0091","1255-P-101A/B To 1255-T-101","Ball","1255-45-0110","3\"-AM.1255.10112-F03N-N","Amine",3,"F03N","300#","STD","RF (125-250 AARH)","None","A 351 CF8","FO (Fail Open)","V","Reduced Bore","Yes","1255-SZSO/C-0091","1255-SDX-0091","No"]
[8,"1255-SDV-0094","Filtration PackageBypass","Ball","1255-45-0111A","3\"-AM.1255.10135-B03N-N","Amine",3,"B03N","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","FO (Fail Open)","V","Reduced Bore","No","1255-SZSO/C-0094","1255-SDX-0094","No"]
[9,"1255-ESDV-0042","1255-P-101 A/BTo 1255-D-103","Ball","1255-45-0105","6\"-AM.1255.10033-F03N-N","Amine",6,"F03N","300#","STD","RF (125-250 AARH)","None","A 351 CF8","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0042","1255-ESDX-0042","No"]
[10,"1255-ESDV-0006","1255-D-101 To 103-D-101","Ball","1255-45-0101","2\"-L.1255.10016-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","FC (Fail Close)","V","Reduced Bore","Yes","1255-EZSO/C-0006","1255-ESDX-0006","No"]
[11,"1255-ESDV-0016","1255-F-101","Ball","1255-45-0102","2\"-L.1255.10004-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","Hot Insulation","A 350 LF2","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0016","1255-ESDX-0016","No"]
[12,"1255-ESDV-0018","1255-F-101","Ball","1255-45-0102","2\"-L.1255.10005-F48-N","Hydrocarbon Liquid",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0018","1255-ESDX-0018","No"]
[13,"1255-ESDV-0026","1255-C-101To 1255-D-103","Ball","1255-45-0103","10\"-AM.1255.10002-F48-N","Amine",10,"F48","300#","S-20","RF (125-250 AARH)","None","A216 WCC","FC (Fail Close)","V","Reduced Bore","Yes","1255-EZSO/C-0026","1255-ESDX-0026","No"]
[14,"1255-ESDV-0028","1255-C-101 To 1255-D-103","Ball","1255-45-0103","2\"-AM.1255.10098-F48-N","Amine",2,"F48","300#","S-80","RF (125-250 AARH)","None","A 350 LF2","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0028","1255-ESDX-0028","No"]
[15,"1255-ESDV-0036","1255-D-102 To 1255-D-103","Ball","1255-45-0104","3\"-AM.1255.10006-F48-N","Amine",3,"F48","300#","STD","RF (125-250 AARH)","None","A216 WCC","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0036","1255-ESDX-0036","No"]
[16,"1255-ESDV-0041","1255-E-101 A/B/CTo 1255-C-102","Ball","1255-45-0107","12\"-AM.1255.10012-B48-H","Amine",12,"B48","600#","S-20","RF (125-250 AARH)","Hot Insulation","A216 WCC","FC (Fail Close)","V","Reduced Bore","Yes","1255-EZSO/C-0041","1255-ESDX-0041","No"]
[17,"1255-ESDV-0066","1255-E-103To 1255-T-101","Ball","1255-45-0106","14\"-AM.1255.10014-B03N-N","Amine",14,"B03N","300#","S-20","RF (125-250 AARH)","None","ASTM A 216WCB","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0066","1255-ESDX-0066","No"]
[18,"1255-ESDV-0076","1255-P-104BDischarge","Ball","1255-45-0108","4\"-CL.1255.12103-D01-P","LP Steam Condensate",4,"D01","300#","STD","RF (125-250 AARH)","Personel Protection","ASTM A 216WCB","FC (Fail Close)","V","Reduced Bore","No","1255-EZSO/C-0076","1255-ESDX-0076","No"]
[19,"1255-ESDV-0081","1255-P-102 A/B To 1255-C-102","Ball","1255-45-0109","3\"-AM.1255.10023-B03S-N","Amine",3,"B03S","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","FO (Fail Open)","V","Reduced Bore","No","1255-EZSO/C-0081","1255-ESDX-0081","No"]
[20,"1255-BDV-0037","Sweet Gas From 1255-D-102 To UNIT 104","Butterfly","1255-45-0104","20\"-G.1255.10018-F23S-N","Hydrocarbon Gas",20,"F23S","300#","S-20","RF (125-250 AARH)","None","A 351 CF8","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0037","1255-BDX-0037","Yes"]
[21,"1255-BDV-0042A","1255-C-103To Steam Boilers","Ball","1255-45-0105","3\"-G.1255.10011-B03S-H","Hydrocarbon Gas",3,"B03S","300#","STD","RF (125-250 AARH)","Hot Insulation","ASTM A 216WCB","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0042A","1255-BDX-0042A","Yes"]
[22,"1255-BDV-0042B","1255-C-103To FS22","Ball","1255-45-0105","3\"-G.1255.10013-B03S-S","Hydrocarbon Gas",3,"B03S","300#","STD","RF (125-250 AARH)","Steam Tracing","ASTM A 216WCB","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0042B","1255-BDX-0042B","Yes"]
[23,"1255-BDV-0043","Fuel GasTo Flash Gas ","Ball","1255-45-0105","2\"-FG.1255.12202-D01-N","Fuel Gas",2,"D01","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0043","1255-BDX-0043","Yes"]
[24,"1255-BDV-0066","NitrogenTo 1255-C-102 outlet","Ball","1255-45-0107","4\"-N.1255.12402-B01-N","Nitrogen",4,"B01","300#","STD","RF (125-250 AARH)","None","ASTM A 216WCB","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0066","1255-BDX-0066","Yes"]
[25,"1255-BDV-0081A","1255-D-104 outletTo FS22","Ball","1255-45-0109","10\"-GA.1255.10006-B03S-S","Acid Gas (H2S+CO2)",10,"B03S","300#","S-20","RF (125-250 AARH)","Steam Tracing","ASTM A 216WCB","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0081A","1255-BDX-0081A","Yes"]
[26,"1255-BDV-0081B","Acid Gas from 1255-D-104To Sulfur Recovery  U108","Ball","1255-45-0109","14\"-GA.1255.10003-B03S-H","Acid Gas (H2S+CO2)",14,"B03S","300#","S-20","RF (125-250 AARH)","Hot Insulation","ASTM A 216WCB","FC (Fail Close)","VI (TSO)","Full Bore","Yes","1255-BZSO/C-0081B","1255-BDX-0081B","Yes"]
[27,"1255-SDV-0037","1255-C-101To 1255-D-102","Butterfly","1255-45-0104","24\"-G.1255.10019-F23S-H","Hydrocarbon Gas",24,"F23S","300#","S-20","RF (125-250 AARH)","Hot Insulation","A 351 CF8","FC (Fail Close)","V","Reduced Bore","No","1255-SZSO/C-0037","1255-SDX-0037","No"]
[28,"1255-SDV-0061","1255-E-103 ByPass","Ball","1255-45-0106","14\"-AM.1255.10054-B03N-N","Amine",14,"B03N","300#","S-20","RF (125-250 AARH)","None","ASTM A 216WCB","FC (Fail Close)","V","Reduced Bore","No","1255-SZSO/C-0061","1255-SDX-0061","No"]
[29,"1255-SDV-0075","CCTo 1255-X-101 ","Ball","1255-45-0108","2\"-CC-101-12101-D01-N","Cold Steam Condensate",2,"D01","300#","S-80","RF (125-250 AARH)","None","ASTM A 105","FC (Fail Close)","V","Reduced Bore","Yes","1255-SZSO/C-0075","1255-SDX-0075","No"]

{"sheet":"OnOff template","index":1,"n_rows":75,"n_cols":35,"rows_kept":75,"cut":false,"hidden":false,"merged":[[63,11,63,14],[64,7,64,10],[64,11,64,14],[63,2,64,6],[54,17,54,22],[54,23,54,29],[31,2,31,4],[31,8,31,10],[43,2,43,6],[43,7,43,14],[44,2,44,6],[44,7,44,14],[43,17,43,22],[43,23,43,29],[44,17,44,22],[44,23,44,29],[57,26,57,29],[26,16,40,16],[39,17,39,22],[37,17,37,21],[37,22,37,29],[38,17,38,20],[38,25,38,26],[7,24,8,25],[0,23,6,29],[70,2,70,28],[71,2,71,28],[72,2,72,28],[73,2,73,28],[74,2,74,28],[7,26,8,27],[7,28,8,29],[7,23,8,23],[66,2,66,6],[66,7,66,14],[63,17,63,22],[63,23,63,29],[64,17,64,22],[64,23,64,29],[65,17,65,22],[65,23,65,29],[66,17,66,22],[66,23,66,29],[50,17,50,22],[50,23,50,29],[42,17,42,22],[42,23,42,29],[65,2,65,6],[65,7,65,14],[60,17,60,20],[61,17,61,22],[51,17,51,22],[45,17,45,22],[57,17,57,19],[57,20,57,22],[57,23,57,25],[53,17,53,22],[53,23,53,29],[55,17,55,22],[55,23,55,29],[56,17,56,22],[49,23,49,25],[49,26,49,29],[49,17,49,19],[49,20,49,22],[52,17,52,22],[52,23,52,29],[47,17,47,22],[47,23,47,29],[56,23,56,29],[63,7,63,10],[14,2,14,9],[15,2,15,9],[16,2,16,9],[17,2,17,9],[18,2,18,9],[23,2,23,9],[24,2,24,4],[24,5,24,9],[25,2,25,9],[30,17,30,22],[30,23,30,29],[48,17,48,29],[61,2,61,6],[62,2,62,6],[53,2,53,6],[55,2,55,6],[55,7,55,14],[56,2,56,6],[45,23,45,29],[46,19,46,22],[46,17,46,18],[46,23,46,25],[46,26,46,29],[61,23,61,29],[62,17,62,22],[62,23,62,29],[58,17,58,29],[59,17,59,20],[59,25,59,29],[46,4,46,6],[51,23,51,29],[41,7,41,14],[42,2,42,6],[42,7,42,14],[45,2,45,6],[45,7,45,14],[62,7,62,14],[26,17,26,22],[26,23,26,29],[27,17,27,22],[27,23,27,29],[28,17,28,18],[28,25,28,29],[28,23,28,24],[29,17,29,22],[29,23,29,29],[57,2,57,14],[41,16,48,16],[59,16,66,16],[58,7,58,14],[58,2,58,6],[59,2,59,6],[59,7,59,14],[60,2,60,6],[38,27,38,29],[37,7,37,14],[38,7,38,14],[39,7,39,14],[37,2,37,6],[38,2,38,6],[39,2,39,6],[56,7,56,14],[40,2,40,14],[48,2,48,14],[54,2,54,14],[50,3,50,4],[50,12,50,14],[51,2,51,6],[51,7,51,14],[52,2,52,6],[52,7,52,14],[46,2,46,3],[46,7,46,9],[46,10,46,14],[47,2,47,6],[47,7,47,14],[49,2,49,6],[49,7,49,14],[41,2,41,6],[29,2,29,6],[29,7,29,14],[30,2,30,6],[30,7,30,9],[30,10,30,12],[30,13,30,14],[35,2,36,5],[35,7,35,14],[36,7,36,14],[31,6,31,7],[31,11,31,12],[32,2,32,6],[33,2,33,6],[34,2,34,6],[32,7,32,14],[33,7,33,14],[34,7,34,14],[31,23,31,29],[32,17,32,22],[32,23,32,29],[12,15,12,16],[26,2,27,6],[28,2,28,6],[28,7,28,14],[19,2,19,9],[20,2,20,9],[21,2,21,9],[22,2,22,9],[23,10,23,13],[23,14,23,17],[18,10,18,13],[18,14,18,17],[14,10,14,13],[14,14,14,17],[25,26,25,29],[20,10,20,13],[20,14,20,17],[20,18,20,21],[20,22,20,25],[20,26,20,29],[31,17,31,22],[10,1,10,2],[11,1,11,2],[12,1,12,2],[69,2,69,28],[10,3,10,29],[11,3,11,14],[12,3,12,14],[11,17,11,29],[12,17,12,29],[11,15,11,16],[58,1,66,1],[59,21,59,23],[60,21,60,23],[60,25,60,29],[60,7,60,14],[61,7,61,14],[55,16,58,16],[53,7,53,14],[49,16,54,16],[50,6,50,7],[50,9,50,10],[45,1,57,1],[29,1,44,1],[38,21,38,24],[26,1,28,1],[28,19,28,22],[24,22,24,23],[24,24,24,25],[25,10,25,13],[25,14,25,17],[25,18,25,21],[25,22,25,25],[26,8,26,14],[27,8,27,14],[40,17,40,29],[41,17,41,22],[41,23,41,29],[35,17,35,21],[35,22,35,29],[36,17,36,21],[36,22,36,29],[34,19,34,22],[33,17,33,29],[34,17,34,18],[34,25,34,29],[34,23,34,24],[39,23,39,29],[23,18,23,21],[23,22,23,25],[23,26,23,29],[24,10,24,13],[24,14,24,15],[24,16,24,17],[24,18,24,19],[24,20,24,21],[21,10,21,13],[21,14,21,17],[21,18,21,21],[21,22,21,25],[21,26,21,29],[22,10,22,13],[22,14,22,17],[22,18,22,21],[22,22,22,25],[22,26,22,29],[18,26,18,29],[19,10,19,13],[19,14,19,15],[19,16,19,17],[19,18,19,19],[19,20,19,21],[16,10,16,13],[16,14,16,17],[16,18,16,21],[16,22,16,25],[16,26,16,29],[17,10,17,13],[17,14,17,17],[17,18,17,21],[17,22,17,25],[17,26,17,29],[19,22,19,23],[19,24,19,25],[19,26,19,27],[19,28,19,29],[9,46,9,55],[13,1,25,1],[13,10,13,13],[13,14,13,17],[13,18,13,21],[13,22,13,25],[13,26,13,29],[0,0,8,6],[0,7,4,22],[5,7,6,9],[5,10,6,22],[7,7,8,10],[7,11,8,22],[14,18,14,21],[14,22,14,25],[14,26,14,29],[15,10,15,13],[15,14,15,17],[15,18,15,21],[15,22,15,25],[15,26,15,29],[9,0,9,29],[18,18,18,21],[18,22,18,25]]}
["Client Logo",null,null,null,null,null,null,"Project Title",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Consultant Logo"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,"Doc Title :"]
[]
[null,null,null,null,null,null,null,"Doc. Number : ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Rev.:",0,null,"Page no.: "]
[]
["On-Off Valve Datasheet"]
[1,"Tag No."]
[2,"P&ID No.:",null,null,null,null,null,null,null,null,null,null,null,null,null,"Service:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"                                                                                                                                                                                                                                                 "]
[3,"Line No.:",null,null,null,null,null,null,null,null,null,null,null,null,null,"Fluid:"]
[null,"PROCESS DATA",null,null,null,null,null,null,null,null,"Units",null,null,null,"Min. Flow",null,null,null,"Normal. Flow",null,null,null,"Max.Flow",null,null,null,"Shut-Off"]
[4,null," Flow Rate",null,null,null,null,null,null,null,"kg/h"]
[5,null," Inlet Pressure",null,null,null,null,null,null,null,"bar(g)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
[6,null," Outlet Pressure",null,null,null,null,null,null,null,"bar(g)"]
[7,null," Inlet Temperature",null,null,null,null,null,null,null,"degC"]
[8,null,"Density/Spec. Grav./Mol Wt.",null,null,null,null,null,null,null,"kg/m3"]
[9,null,"Viscosity",null,null,"Spec Heats Ratio",null,null,null,null,"cP"]
[10,null,"Vapor Pressure Pv",null,null,null,null,null,null,null,"bar(g)"]
[11,null,"Gas Compressibility Factor"]
[12,null,"Required Cv"]
[13,null,"Position @calc. Cv",null,null,null,null,null,null,null,"%"]
[14,null,"Allowable",null,null,"Predicted SPL",null,null,null,null,"db(A)",null,null,null,"< 85",null,null,null,"< 85",null,null,null,"< 85"]
[15,null,"Critical Pressure",null,null,null,null,null,null,null,"bar(g)"]
[16,"LINE","Line Size/Sch/Pipe Class",null,null,null,null,"In",null,null,null,null,null,null,null,57,"ACTUATOR","Type",null,null,null,null,null,"Pneumatic-Piston"]
[17,null,null,null,null,null,null,"Out",null,null,null,null,null,null,null,58,null,"Mfr & Model"]
[18,null,"Line Insulation",null,null,null,null,null,null,null,null,null,null,null,null,59,null,"Size",null,"VTA",null,null,null,"Eff Area",null,"VTA"]
[19,"VALVE BODY ","Type",null,null,null,null,null,null,null,null,null,null,null,null,60,null,"Application Type",null,null,null,null,null,"On/Off"]
[20,null,"Size",null,null,null,null,null,null,null,"ANSI Class",null,null,null,null,61,null,"Spring Action Open/Close"]
[21,null,"Max Press.",null,null,null," bar g",null,"Max Temp",null,null,null,null,"deg C",null,62,null,"Max Allowable Pressure",null,null,null,null,null,"VTA"]
[22,null,"Mfr & Model",null,null,null,null,null,null,null,null,null,null,null,null,63,null,"Min Required Pressure",null,null,null,null,null,"VTA"]
[23,null,"Body material",null,null,null,null,null,null,null,null,null,null,null,null,64,null,"Avalable Air Supply Pressure :"]
[24,null,"Bonnet Material",null,null,null,null,null,null,null,null,null,null,null,null,65,null,"Max",null,"9 bar g",null,null,null,"Min",null,"4.5 bar g"]
[25,null,"End Connection",null,null,null,"In",null,null,null,null,null,null,null,null,66,null,"Bench Range",null,null,null,null,"VTA"]
[26,null,null,null,null,null,"Out",null,null,null,null,null,null,null,null,67,null,"Actuator Orientation",null,null,null,null,"VTA"]
[27,null,"Flange Face Finish",null,null,null,null,null,null,null,null,null,null,null,null,68,null,"Handwheel Type"]
[28,null,"Flow Direction",null,null,null,null,"VTA",null,null,null,null,null,null,null,69,null,"Air Failure Valve",null,null,null,"NO",null,null,null,"Set at",null,"N/A"]
[29,null,"Type of Bonnet",null,null,null,null,"Standard",null,null,null,null,null,null,null,70,null,"DP for Act. Sizing",null,null,null,null,null,{"$f":"AA16","v":8}]
[30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,71]
[31,null,"Packing Material",null,null,null,null,"Graphite",null,null,null,null,null,null,null,72,"POSITIONER","Input Signal",null,null,null,null,null,"N/A"]
[32,null,"Packing Type",null,null,null,null,"VTA",null,null,null,null,null,null,null,73,null,"Type",null,null,null,null,null,"N/A"]
[33,null,"Fire safe & Anti static",null,null,null,null,"Yes, API 607, API Spec. 6FA .",null,null,null,null,null,null,null,74,null,"Mfr & Model"]
[34,null,"Packing Type",null,null,null,null,"VTA",null,null,null,null,null,null,null,75,null,"Case Material",null,null,null,null,null,"N/A"]
[35,"TRIM","Type",null,null,null,null,null,null,null,null,null,null,null,null,76,null,"On Increase Signal Output",null,null,null,null,null,"N/A"]
[36,null,"Size",null,"VTA",null,null,"Rated Travel",null,null,"VTA",null,null,null,null,77,null,"Gauges",null,"VTA",null,null,null,"N/A",null,null,"N/A"]
[37,null,"Characteristic",null,null,null,null,"Quick Opening",null,null,null,null,null,null,null,78,null,"Cam Characteristic",null,null,null,null,null,"N/A"]
[38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79]
[39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,"SWITCH","Type",null,null,"Reed ",null,null,"Quantity ",null,null,2]
[40,null,"Rate","VTA",null,"Cv","VTA",null,"Fl","VTA",null,"Xt","VTA",null,null,81,null,"Mfr & Model"]
[41,null,"Ball / Disk/ Plug",null,null,null,null,"316SS (VTC)",null,null,null,null,null,null,null,82,null,"Contacts/Rating",null,null,null,null,null,"SPDT / 1 Amp/24V DC"]
[42,null,"Seat Material / Type",null,null,null,null,"316SS (VTC) / VTA",null,null,null,null,null,null,null,83,null,"Actuation Points",null,null,null,null,null,"Full close / Full open"]
[43,null,"Cage/Guide Material",null,null,null,null,"316SS (VTC)",null,null,null,null,null,null,null,84,null,"Tag Number(s)"]
[44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,85,null,"Electrical Connection",null,null,null,null,null,"ISO M20"]
[45,null,"Stem Material /Type",null,null,null,null,"316SS (VTC) / Anti Blow Out",null,null,null,null,null,null,null,86,"AIR","Mfr & Model"]
[46,null,"ANSI/FCI Leakage Class",null,null,null,null,null,null,null,null,null,null,null,null,87,null,"Set Pressure",null,null,null,null,null,"VTA"]
[47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,88,null,"Filter",null,null,"Yes",null,null,"Gauge",null,null,"Yes"]
[48,"SPECIAL","IEC Class",null,null,null,null,"Group II B, Class T3",null,null,null,null,null,null,null,89]
[49,null,"Insolation Class",null,null,null,null,"IP55 (for pneumatic), IP65 (For Electronic)",null,null,null,null,null,null,null,90,"ACCESSORIES","I/P Reqd?",null,null,null,"No",null,null,"Tag"]
[50,null,"Tubing",null,null,null,null,"Imperial AISI 904L, 1/4\" OD NPT",null,null,null,null,null,null,null,91,null,"Solenoid Reqd?",null,null,null,"Yes",null,null,"Tag"]
[51,null,"Fitting",null,null,null,null,"Swagelok/Alok AISI 316L",null,null,null,null,null,null,null,92,null,"Mfr & Model"]
[52,null,"Elec. Conn.",null,null,null,null,"ISO  M20×1.5",null,null,null,null,null,null,null,93,null,"Air Accumulator?",null,null,null,"No",null,"No"]
[53,null,"Operating Time",null,null,null,null,"Opening",null,null,null,null,null,null,null,94]
[54,null,null,null,null,null,null,"Closing",null,null,null,null,null,null,null,95]
[55,null,null,null,null,null,null,null,null,null,null,null,null,null,null,96]
[56,null,null,null,null,null,null,null,null,null,null,null,null,null,null,97]
["NOTES :"]
[]
[null,"1."," VTA: Vendor To Advise   VTC: Vendor To Confirm  N/A: Not Applicable"]
[null,"2."]
[null,"3."]
[null,"4."]
[null,"5."]
[null,"6."]